## VAVList
AHU | VAV | feeds | Zone_Air_Temperature_Setpoint | Zone_Air_Temperature_Sensor | Supply_Air_Flow_Setpoint | Supply_Air_Flow_Sensor
AH2 | S1-01_VAV | 132_MECH_STEAM | 1 | 1 | 0 | 1
AH2 | S1-02_VAV | 148_C&S_COMPUTER | 2 | 2 | 0 | 1
AH2 | S1-03_VAV | 170_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S1-04_VAV | 149_MDC_MECH | 1 | 1 | 0 | 1
AH2 | S1-05_VAV | 171_RISER_CLOSET | 0 | 1 | 0 | 1
AH2 | S1-06_VAV | 175_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S1-07_VAV | 177_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S1-08_VAV | 160_CORRIDOR | 1 | 1 | 0 | 1
AH2 | S1-09_VAV | 168_PLUMBING | 1 | 1 | 0 | 1
AH2 | S1-10_VAV | 148_C&S_COMPUTER | 2 | 2 | 0 | 1
AH2 | S1-13_VAV | Room_133B | 1 | 1 | 0 | 1
AH2 | S1-14_VAV | 133A_Server_Room | 0 | 1 | 0 | 1
AH2 | S1-15_VAV | 137_Lab | 0 | 1 | 0 | 1
AH2 | S1-15_VAV | Room_137_Lab | 0 | 1 | 0 | 1
AH2 | S1-16_VAV | Room_133 | 1 | 1 | 0 | 1
AH2 | S1-17_VAV | 135_Game_Design | 1 | 1 | 0 | 1
AH2 | S1-18_VAV | 131_Tele-Health | 1 | 1 | 0 | 1
AH2 | S1-19_VAV | Room_141 | 2 | 2 | 0 | 1
AH2 | S1-20_VAV | Room_141 | 2 | 2 | 0 | 1
AH2 | S1-22_VAV | - | 0 | 0 | 0 | 0
AH2 | S1-23_VAV | - | 0 | 0 | 0 | 0
AH2 | S2-01_VAV | 213_VESTIBULE | 1 | 1 | 0 | 1
AH2 | S2-02_VAV | 212_HALLWAY | 1 | 1 | 0 | 1
AH2 | S2-03_VAV | 222_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S2-04_VAV | 238_BREAK_OUT | 1 | 1 | 0 | 1
AH2 | S2-05_VAV | 240_CLASSROOM | 1 | 1 | 0 | 1
AH2 | S2-06_VAV | 250_CLASSROOM | 1 | 1 | 0 | 1
AH2 | S2-07_VAV | 270_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S2-08_VAV | 271_RISER_CLOSET | 0 | 1 | 0 | 1
AH2 | S2-09_VAV | 275_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S2-10_VAV | 266C_OFFICE | 1 | 1 | 0 | 1
AH2 | S2-11_VAV | 254_CLASSROOM | 1 | 1 | 0 | 1
AH2 | S2-12_VAV | 260_HALLWAY | 1 | 1 | 0 | 1
AH2 | S2-13_VAV | 266_RECEIVING | 1 | 1 | 0 | 1
AH2 | S2-14_VAV | 277_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S2-15_VAV | CYBERCAFE_210 | 2 | 2 | 0 | 1
AH2 | S2-16_VAV | CYBERCAFE_210 | 2 | 2 | 0 | 1
AH2 | S2-17_VAV | CYBERCAFE_210A | 1 | 1 | 0 | 1
AH2 | S2-18_VAV | KITCHEN_214 | 1 | 1 | 0 | 1
AH2 | S2-19_VAV | COMP_LAB_200 | 1 | 1 | 0 | 1
AH2 | S2-20_VAV | COMP_LAB_200A | 1 | 1 | 0 | 1
AH2 | S2-21_VAV | COMP_LAB_200AA | 1 | 1 | 0 | 1
AH2 | S3-01_VAV | 300_PRE_LOBBY | 2 | 2 | 0 | 1
AH2 | S3-02_VAV | 306_BREAK_OUT | 1 | 1 | 0 | 1
AH2 | S3-03_VAV | 330F_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-04_VAV | 330E_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-05_VAV | 330C_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-06_VAV | 330B_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-07_VAV | 310_AUDITORIUM | 2 | 2 | 0 | 1
AH2 | S3-08_VAV | 330_LEARNING | 1 | 1 | 0 | 1
AH2 | S3-09_VAV | 310_AUDITORIUM | 2 | 2 | 0 | 1
AH2 | S3-10_VAV | 340_LOBBY | 1 | 1 | 0 | 1
AH2 | S3-11_VAV | 300_PRE_LOBBY | 2 | 2 | 0 | 1
AH2 | S3-12_VAV | 370_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S3-13_VAV | 371_IDF_CLOSET | 0 | 1 | 0 | 1
AH2 | S3-14_VAV | 375_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S3-15_VAV | 345_DISPLAY | 1 | 1 | 0 | 1
AH2 | S3-16_VAV | 356D_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-17_VAV | 356_OPEN_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-18_VAV | 377_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S3-19_VAV | 356F_OFFICE | 1 | 1 | 0 | 1
AH2 | S3-20_VAV | 361_EXIT_PASSAGE | 1 | 1 | 0 | 1
AH2 | S3-21_VAV | 368_CONFERENCE | 1 | 1 | 0 | 1
AH2 | S4-01_VAV | 413_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-02_VAV | 432_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-03_VAV | 434_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-04_VAV | 440_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-05_VAV | 446_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-06_VAV | 421_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-07_VAV | 424_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-08_VAV | 423_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-09_VAV | 448_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-10_VAV | 429_EMER_ELECT | 0 | 2 | 0 | 2
AH2 | S4-11_VAV | 470_ELEV_LOBBY | 1 | 2 | 0 | 2
AH2 | S4-12_VAV | 450_OPEN_OFFICE | 2 | 4 | 0 | 2
AH2 | S4-13_VAV | 450_OPEN_OFFICE | 2 | 4 | 0 | 2
AH2 | S4-14_VAV | 471_RISER_CLOSET | 0 | 2 | 0 | 2
AH2 | S4-15_VAV | 458_CONFERENCE | 1 | 2 | 0 | 2
AH2 | S4-16_VAV | 464_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-17_VAV | 475_ELECTRICAL | 0 | 2 | 0 | 2
AH2 | S4-18_VAV | 460_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-19_VAV | 477_WOMENS_BATH | 1 | 2 | 0 | 2
AH2 | S4-20_VAV | 466_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S4-21_VAV | 468_OPEN_OFFICE | 1 | 2 | 0 | 2
AH2 | S5-01_VAV | 510_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-02_VAV | 511_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-03_VAV | 532_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S5-04_VAV | 532_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S5-05_VAV | 538_OPEN_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-06_VAV | 515_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-07_VAV | 548_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S5-08_VAV | 520_MICROFAB_OFF | 1 | 1 | 0 | 1
AH2 | S5-09_VAV | 500_HALLWAY | 1 | 1 | 0 | 1
AH2 | S5-10_VAV | 520C_MICROFB_OFF | 1 | 1 | 0 | 1
AH2 | S5-11_VAV | 570_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S5-12_VAV | 550_OPEN_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-13_VAV | 548_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S5-14_VAV | 554_CONFERENCE | 1 | 1 | 0 | 1
AH2 | S5-15_VAV | 571_RISER_CLOSET | 0 | 1 | 0 | 1
AH2 | S5-16_VAV | 558_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-17_VAV | 575_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S5-18_VAV | 568_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S5-19_VAV | 577_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S5-20_VAV | 566_OPEN_OFFICE | 1 | 1 | 0 | 1
AH2 | S5-21_VAV | 568_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S6-01_VAV | 630_CONFERENCE | 1 | 1 | 0 | 1
AH2 | S6-02_VAV | 640_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-03_VAV | 646_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-04_VAV | 630B_PANTRY | 1 | 1 | 0 | 1
AH2 | S6-05_VAV | 630A_LOUNGE | 1 | 1 | 0 | 1
AH2 | S6-06_VAV | 621C_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-07_VAV | 621A_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-08_VAV | 621_OPN_RESEARCH | 2 | 2 | 0 | 1
AH2 | S6-09_VAV | 629_EMER_ELECT | 0 | 1 | 0 | 1
AH2 | S6-10_VAV | 621_OPN_RESEARCH | 2 | 2 | 0 | 1
AH2 | S6-11_VAV | 670_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S6-12_VAV | 652_CUBICLES | 1 | 1 | 0 | 1
AH2 | S6-13_VAV | 652A_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-14_VAV | 671_IDF_CLOSET | 0 | 1 | 0 | 1
AH2 | S6-15_VAV | 656B_OFFICE | 1 | 1 | 0 | 1
AH2 | S6-16_VAV | 675_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S6-17_VAV | 656_CUBICLES | 1 | 1 | 0 | 1
AH2 | S6-18_VAV | 677_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S6-19_VAV | 650_HALLWAY | 1 | 1 | 0 | 1
AH2 | S6-20_VAV | 668_RESEARCH | 1 | 1 | 0 | 1
AH2 | S7-01_VAV | 736_OPEN_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-02_VAV | 730_CONFERENCE | 1 | 1 | 0 | 1
AH2 | S7-03_VAV | 738_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S7-04_VAV | 738_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S7-05_VAV | 725_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-06_VAV | 721_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-07_VAV | 770_ELEV_LOBBY | 1 | 1 | 0 | 1
AH2 | S7-08_VAV | 722_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-09_VAV | 750_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S7-10_VAV | 750_OPEN_OFFICE | 2 | 2 | 0 | 1
AH2 | S7-11_VAV | 771_RISER_CLOSET | 0 | 1 | 0 | 1
AH2 | S7-12_VAV | 775_ELECTRICAL | 0 | 1 | 0 | 1
AH2 | S7-13_VAV | 756_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-14_VAV | 766_OFFICE | 1 | 1 | 0 | 1
AH2 | S7-15_VAV | 777_WOMENS_BATH | 1 | 1 | 0 | 1
AH2 | S7-16_VAV | 768_OPEN_OFFICE | 1 | 1 | 0 | 1
Some VAVs don't have Setpoint?
*Green means the room fed by multiple VAVs.
*Red means multiple points of one VAV.
*Yellow means no point of one VAV.

## AHUList
AHU | AH2A | AH2B
AH2 | AH2A_Cooling_Coil | AH2B_Cooling_Coil
AH2 | AH2A_Damper | AH2B_Damper
AH2 | AH2A_Exhaust_Fan | AH2B_Exhaust_Fan
AH2 |  | AH2B_ISO_DAMPER
AH2 | AH2A_Outside_Damper | AH2B_Outside_Damper
AH2 | AH2A_RF_VFD | AH2B_RF_VFD
AH2 | AH2A_Return_Fan | AH2B_Return_Fan
AH2 | AH2A_SF_VFD | AH2B_SF_VFD
AH2 | AH2A_Supply_Fan | AH2B_Supply_Fan
The following triplet is missing,
sdh:AH2 brick:hasPart sdh:AH2A,
sdh:AH2B .
*While AH2B has "ISO_DAMPER", AH2A doesn't have it.

## SameRoom
| 137_Lab | Room_137_Lab
type | n3e65878f4cc04798941665aa2971e98eb764
type | n3e65878f4cc04798941665aa2971e98eb476
type | n3e65878f4cc04798941665aa2971e98eb1892 | n3e65878f4cc04798941665aa2971e98eb476
type | n3e65878f4cc04798941665aa2971e98eb487 | n3e65878f4cc04798941665aa2971e98eb1892
type | n3e65878f4cc04798941665aa2971e98eb280 | n3e65878f4cc04798941665aa2971e98eb280
type | n3e65878f4cc04798941665aa2971e98eb1208
type | n3e65878f4cc04798941665aa2971e98eb4988
type | n3e65878f4cc04798941665aa2971e98eb1893 | n3e65878f4cc04798941665aa2971e98eb1893
type | n3e65878f4cc04798941665aa2971e98eb4171
type | n3e65878f4cc04798941665aa2971e98eb4172
type |  | n3e65878f4cc04798941665aa2971e98eb1894
type | Thing | Thing
type | Class | Class
type | HVAC_Zone | HVAC_Zone
type | Laboratory
type | Location | Location
type | Room
type | Space
type | Zone | Zone
hasPoint | S1-15:RM_STPT_MAX
hasPoint | S1-15:RM_STPT_MIN
hasPoint | S1-15:STPT_DIAL_Status
hasPoint | S1-15_ROOM_TEMP
hasPoint |  | S1-15:RM_STPT_DIAL
hasTag | HVAC | HVAC
hasTag | Laboratory
hasTag | Location | Location
hasTag | Room
hasTag | Space
hasTag | Zone | Zone
isFedBy | S1-15_VAV | S1-15_VAV
isPartOf | Floor_1
Some people used different name when they labeled it.
Same room?
*Laboratory/Room/Space
*Different points
*Floor 1?

## NoPrefix
<https://brickschema.org/schema/building_example#148_C&S_COMPUTER>
It doesn't have prefix because of "&".

## Identification1
| S3-07_VAV | S3-09_VAV |  | S3-07_ROOM_TEMP | S3-09_ROOM_TEMP
type | n88ed94ae00c54874be548bf30b7b40c0b2557 | n88ed94ae00c54874be548bf30b7b40c0b2557 | type | n8c47ecc96f5c40e295b89ddbb4442790b1696 | n8c47ecc96f5c40e295b89ddbb4442790b1696
type | n88ed94ae00c54874be548bf30b7b40c0b1892 | n88ed94ae00c54874be548bf30b7b40c0b1892 | type | n8c47ecc96f5c40e295b89ddbb4442790b476 | n8c47ecc96f5c40e295b89ddbb4442790b476
type | n88ed94ae00c54874be548bf30b7b40c0b837 | n88ed94ae00c54874be548bf30b7b40c0b837 | type | n8c47ecc96f5c40e295b89ddbb4442790b346 | n8c47ecc96f5c40e295b89ddbb4442790b346
type | n88ed94ae00c54874be548bf30b7b40c0b1647 | n88ed94ae00c54874be548bf30b7b40c0b1647 | type | n8c47ecc96f5c40e295b89ddbb4442790b385 | n8c47ecc96f5c40e295b89ddbb4442790b385
type | n88ed94ae00c54874be548bf30b7b40c0b5351 | n88ed94ae00c54874be548bf30b7b40c0b5351 | type | n8c47ecc96f5c40e295b89ddbb4442790b234 | n8c47ecc96f5c40e295b89ddbb4442790b234
type | n88ed94ae00c54874be548bf30b7b40c0b954 | n88ed94ae00c54874be548bf30b7b40c0b954 | type | n8c47ecc96f5c40e295b89ddbb4442790b3196 | n8c47ecc96f5c40e295b89ddbb4442790b3196
type | n88ed94ae00c54874be548bf30b7b40c0b241 | n88ed94ae00c54874be548bf30b7b40c0b241 | type | n8c47ecc96f5c40e295b89ddbb4442790b5362 | n8c47ecc96f5c40e295b89ddbb4442790b5362
type | n88ed94ae00c54874be548bf30b7b40c0b6202 | n88ed94ae00c54874be548bf30b7b40c0b6202 | type | n8c47ecc96f5c40e295b89ddbb4442790b3677 | n8c47ecc96f5c40e295b89ddbb4442790b3677
type | n88ed94ae00c54874be548bf30b7b40c0b6203 | n88ed94ae00c54874be548bf30b7b40c0b6203 | type | n8c47ecc96f5c40e295b89ddbb4442790b3696 | n8c47ecc96f5c40e295b89ddbb4442790b3696
type | n88ed94ae00c54874be548bf30b7b40c0b6204 | n88ed94ae00c54874be548bf30b7b40c0b6204 | type | n8c47ecc96f5c40e295b89ddbb4442790b3715 | n8c47ecc96f5c40e295b89ddbb4442790b3715
type | n88ed94ae00c54874be548bf30b7b40c0b6205 | n88ed94ae00c54874be548bf30b7b40c0b6205 | type | n8c47ecc96f5c40e295b89ddbb4442790b2726 | n8c47ecc96f5c40e295b89ddbb4442790b2726
type | n88ed94ae00c54874be548bf30b7b40c0b6206 | n88ed94ae00c54874be548bf30b7b40c0b6206 | type | n8c47ecc96f5c40e295b89ddbb4442790b3242 | n8c47ecc96f5c40e295b89ddbb4442790b3242
type | n88ed94ae00c54874be548bf30b7b40c0b4996 | n88ed94ae00c54874be548bf30b7b40c0b4996 | type | n8c47ecc96f5c40e295b89ddbb4442790b5363 | n8c47ecc96f5c40e295b89ddbb4442790b5363
type | n88ed94ae00c54874be548bf30b7b40c0b4997 | n88ed94ae00c54874be548bf30b7b40c0b4997 | type | n8c47ecc96f5c40e295b89ddbb4442790b4014 | n8c47ecc96f5c40e295b89ddbb4442790b4014
type | n88ed94ae00c54874be548bf30b7b40c0b1909 | n88ed94ae00c54874be548bf30b7b40c0b1909 | type | n8c47ecc96f5c40e295b89ddbb4442790b3064 | n8c47ecc96f5c40e295b89ddbb4442790b3064
type | n88ed94ae00c54874be548bf30b7b40c0b6207 | n88ed94ae00c54874be548bf30b7b40c0b6207 | type | n8c47ecc96f5c40e295b89ddbb4442790b3078 | n8c47ecc96f5c40e295b89ddbb4442790b3078
type | Thing | Thing | type | n8c47ecc96f5c40e295b89ddbb4442790b4297 | n8c47ecc96f5c40e295b89ddbb4442790b4297
type | Class | Class | type | n8c47ecc96f5c40e295b89ddbb4442790b5364 | n8c47ecc96f5c40e295b89ddbb4442790b5364
type | Equipment | Equipment | type | n8c47ecc96f5c40e295b89ddbb4442790b5047 | n8c47ecc96f5c40e295b89ddbb4442790b5047
type | HVAC_Equipment | HVAC_Equipment | type | n8c47ecc96f5c40e295b89ddbb4442790b5365 | n8c47ecc96f5c40e295b89ddbb4442790b5365
type | RVAV | RVAV | type | n8c47ecc96f5c40e295b89ddbb4442790b5366 | n8c47ecc96f5c40e295b89ddbb4442790b5366
type | Terminal_Unit | Terminal_Unit | type | n8c47ecc96f5c40e295b89ddbb4442790b5290 | n8c47ecc96f5c40e295b89ddbb4442790b5290
type | VAV | VAV | type | n8c47ecc96f5c40e295b89ddbb4442790b5367 | n8c47ecc96f5c40e295b89ddbb4442790b5367
type | Variable_Air_Volume_Box | Variable_Air_Volume_Box | type | n8c47ecc96f5c40e295b89ddbb4442790b5368 | n8c47ecc96f5c40e295b89ddbb4442790b5368
type | Variable_Air_Volume_Box_With_Reheat | Variable_Air_Volume_Box_With_Reheat | type | n8c47ecc96f5c40e295b89ddbb4442790b5369 | n8c47ecc96f5c40e295b89ddbb4442790b5369
feeds | 310_AUDITORIUM | 310_AUDITORIUM | type | n8c47ecc96f5c40e295b89ddbb4442790b5370 | n8c47ecc96f5c40e295b89ddbb4442790b5370
hasPoint | S3-07:AIR_VOLUME | S3-09:AIR_VOLUME | type | n8c47ecc96f5c40e295b89ddbb4442790b4241 | n8c47ecc96f5c40e295b89ddbb4442790b4241
hasPoint | S3-07:CLG_FLOW_MAX | S3-09:CLG_FLOW_MAX | type | n8c47ecc96f5c40e295b89ddbb4442790b4250 | n8c47ecc96f5c40e295b89ddbb4442790b4250
hasPoint | S3-07:CLG_FLOW_MIN | S3-09:CLG_FLOW_MIN | type | n8c47ecc96f5c40e295b89ddbb4442790b5271 | n8c47ecc96f5c40e295b89ddbb4442790b5271
hasPoint | S3-07:CLG_LOOPOUT | S3-09:CLG_LOOPOUT | type | n8c47ecc96f5c40e295b89ddbb4442790b5371 | n8c47ecc96f5c40e295b89ddbb4442790b5371
hasPoint | S3-07:CTL_FLOW_MAX | S3-09:CTL_FLOW_MAX | type | n8c47ecc96f5c40e295b89ddbb4442790b5372 | n8c47ecc96f5c40e295b89ddbb4442790b5372
hasPoint | S3-07:CTL_FLOW_MIN | S3-09:CTL_FLOW_MIN | type | n8c47ecc96f5c40e295b89ddbb4442790b5373 | n8c47ecc96f5c40e295b89ddbb4442790b5373
hasPoint | S3-07:CTL_STPT | S3-09:CTL_STPT | type | n8c47ecc96f5c40e295b89ddbb4442790b5344 | n8c47ecc96f5c40e295b89ddbb4442790b5344
hasPoint | S3-07:DAY_CLG_STPT | S3-09:DAY_CLG_STPT | type | n8c47ecc96f5c40e295b89ddbb4442790b5345 | n8c47ecc96f5c40e295b89ddbb4442790b5345
hasPoint | S3-07:DAY_HTG_STPT | S3-09:DAY_HTG_STPT | type | n8c47ecc96f5c40e295b89ddbb4442790b5374 | n8c47ecc96f5c40e295b89ddbb4442790b5374
hasPoint | S3-07:DAY_NGT | S3-09:DAY_NGT | type | n8c47ecc96f5c40e295b89ddbb4442790b5375 | n8c47ecc96f5c40e295b89ddbb4442790b5375
hasPoint | S3-07:DMPR_COMD | S3-09:DMPR_COMD | type | n8c47ecc96f5c40e295b89ddbb4442790b5376 | n8c47ecc96f5c40e295b89ddbb4442790b5376
hasPoint | S3-07:DMPR_POS | S3-09:DMPR_POS | type | n8c47ecc96f5c40e295b89ddbb4442790b5346 | n8c47ecc96f5c40e295b89ddbb4442790b5346
hasPoint | S3-07:HEAT_COOL | S3-09:HEAT_COOL | type | n8c47ecc96f5c40e295b89ddbb4442790b5377 | n8c47ecc96f5c40e295b89ddbb4442790b5377
hasPoint | S3-07:HTG_FLOW_MAX | S3-09:HTG_FLOW_MAX | type | n8c47ecc96f5c40e295b89ddbb4442790b1903 | n8c47ecc96f5c40e295b89ddbb4442790b1903
hasPoint | S3-07:HTG_FLOW_MIN | S3-09:HTG_FLOW_MIN | type | n8c47ecc96f5c40e295b89ddbb4442790b2205 | n8c47ecc96f5c40e295b89ddbb4442790b2205
hasPoint | S3-07:HTG_LOOPOUT | S3-09:HTG_LOOPOUT | type | n8c47ecc96f5c40e295b89ddbb4442790b5378 | n8c47ecc96f5c40e295b89ddbb4442790b5378
hasPoint | S3-07:NGT_CLG_STPT | S3-09:NGT_CLG_STPT | type | n8c47ecc96f5c40e295b89ddbb4442790b2337 | n8c47ecc96f5c40e295b89ddbb4442790b2337
hasPoint | S3-07:NGT_HTG_STPT | S3-09:NGT_HTG_STPT | type | n8c47ecc96f5c40e295b89ddbb4442790b1201 | n8c47ecc96f5c40e295b89ddbb4442790b1201
hasPoint | S3-07:SWITCH_DBAND | S3-09:SWITCH_DBAND | type | n8c47ecc96f5c40e295b89ddbb4442790b528 | n8c47ecc96f5c40e295b89ddbb4442790b528
hasPoint | S3-07:VLV_COMD | S3-09:VLV_COMD | type | n8c47ecc96f5c40e295b89ddbb4442790b1417 | n8c47ecc96f5c40e295b89ddbb4442790b1417
hasPoint | S3-07:VLV_POS | S3-09:VLV_POS | type | n8c47ecc96f5c40e295b89ddbb4442790b5379 | n8c47ecc96f5c40e295b89ddbb4442790b5379
hasTag | Box | Box | type | n8c47ecc96f5c40e295b89ddbb4442790b1455 | n8c47ecc96f5c40e295b89ddbb4442790b1455
hasTag | Equipment | Equipment | type | n8c47ecc96f5c40e295b89ddbb4442790b1522 | n8c47ecc96f5c40e295b89ddbb4442790b1522
hasTag | HVAC | HVAC | type | n8c47ecc96f5c40e295b89ddbb4442790b1613 | n8c47ecc96f5c40e295b89ddbb4442790b1613
hasTag | RVAV | RVAV | type | n8c47ecc96f5c40e295b89ddbb4442790b5380 | n8c47ecc96f5c40e295b89ddbb4442790b5380
hasTag | Reheat | Reheat | type | n8c47ecc96f5c40e295b89ddbb4442790b3808 | n8c47ecc96f5c40e295b89ddbb4442790b3808
hasTag | Terminal | Terminal | type | n8c47ecc96f5c40e295b89ddbb4442790b3969 | n8c47ecc96f5c40e295b89ddbb4442790b3969
hasTag | Unit | Unit | type | n8c47ecc96f5c40e295b89ddbb4442790b2993 | n8c47ecc96f5c40e295b89ddbb4442790b2993
hasTag | VAV | VAV | type | n8c47ecc96f5c40e295b89ddbb4442790b4124 | n8c47ecc96f5c40e295b89ddbb4442790b4124
hasTag | Variable | Variable | type | n8c47ecc96f5c40e295b89ddbb4442790b5349 | n8c47ecc96f5c40e295b89ddbb4442790b5349
hasTag | Volume | Volume | type | n8c47ecc96f5c40e295b89ddbb4442790b4219 | n8c47ecc96f5c40e295b89ddbb4442790b4219
isFedBy | AH2 | AH2 | type | Thing | Thing
isFedBy | Heat_Exchanger_System | Heat_Exchanger_System | type | Air_Temperature_Sensor | Air_Temperature_Sensor
|  |  | type | Class | Class
|  |  | type | Point | Point
|  |  | type | Sensor | Sensor
|  |  | type | Temperature_Sensor | Temperature_Sensor
|  |  | type | Zone_Air_Temperature_Sensor | Zone_Air_Temperature_Sensor
|  |  | bacnetPoint | id-7408-164-analogInput | id-7408-172-analogInput
|  |  | hasTag | Air | Air
|  |  | hasTag | Point | Point
|  |  | hasTag | Sensor | Sensor
|  |  | hasTag | Temperature | Temperature
|  |  | hasTag | Zone | Zone
|  |  | hasUnit | http://qudt.org/vocab/unit/DEG_F | http://qudt.org/vocab/unit/DEG_F
|  |  | isPointOf | 310_AUDITORIUM | 310_AUDITORIUM
|  |  | measures | Air | Air
|  |  | measures | Temperature | Temperature
|  |  | measures | Zone_Air | Zone_Air
We can not identify these nodes, except for using node names.

## Identification2
| S4-12_VAV | S4-13_VAV |  | S4-12_ROOM_TEMP | S4-13_ROOM_TEMP |  | id-7408-262-analogInput | id-7408-31-analogInput | id-7408-266-analogInput | id-7408-34-analogInput
type | n2b20ded59b5f471d97db4c4dc91918efb2557 | n2b20ded59b5f471d97db4c4dc91918efb2557 | type | n52afc3a389444a5e927b8c21689ca32cb1696 | n52afc3a389444a5e927b8c21689ca32cb1696 | type | Thing | Thing | Thing | Thing
type | n2b20ded59b5f471d97db4c4dc91918efb1892 | n2b20ded59b5f471d97db4c4dc91918efb1892 | type | n52afc3a389444a5e927b8c21689ca32cb476 | n52afc3a389444a5e927b8c21689ca32cb476 | type | BACnetReference | BACnetReference | BACnetReference | BACnetReference
type | n2b20ded59b5f471d97db4c4dc91918efb837 | n2b20ded59b5f471d97db4c4dc91918efb837 | type | n52afc3a389444a5e927b8c21689ca32cb346 | n52afc3a389444a5e927b8c21689ca32cb346 | accessedAt | BACnet-77:0x000000004a08 | BACnet-77:0x000000004a08 | BACnet-77:0x000000004a08 | BACnet-77:0x000000004a08
type | n2b20ded59b5f471d97db4c4dc91918efb1647 | n2b20ded59b5f471d97db4c4dc91918efb1647 | type | n52afc3a389444a5e927b8c21689ca32cb385 | n52afc3a389444a5e927b8c21689ca32cb385 | hasBacnetDeviceInstance | 262 | 31 | 266 | 34
type | n2b20ded59b5f471d97db4c4dc91918efb5351 | n2b20ded59b5f471d97db4c4dc91918efb5351 | type | n52afc3a389444a5e927b8c21689ca32cb234 | n52afc3a389444a5e927b8c21689ca32cb234 | hasBacnetDeviceType | analogInput | analogInput | analogInput | analogInput
type | n2b20ded59b5f471d97db4c4dc91918efb954 | n2b20ded59b5f471d97db4c4dc91918efb954 | type | n52afc3a389444a5e927b8c21689ca32cb3196 | n52afc3a389444a5e927b8c21689ca32cb3196
type | n2b20ded59b5f471d97db4c4dc91918efb241 | n2b20ded59b5f471d97db4c4dc91918efb241 | type | n52afc3a389444a5e927b8c21689ca32cb5362 | n52afc3a389444a5e927b8c21689ca32cb5362
type | n2b20ded59b5f471d97db4c4dc91918efb6202 | n2b20ded59b5f471d97db4c4dc91918efb6202 | type | n52afc3a389444a5e927b8c21689ca32cb3677 | n52afc3a389444a5e927b8c21689ca32cb3677
type | n2b20ded59b5f471d97db4c4dc91918efb6203 | n2b20ded59b5f471d97db4c4dc91918efb6203 | type | n52afc3a389444a5e927b8c21689ca32cb3696 | n52afc3a389444a5e927b8c21689ca32cb3696
type | n2b20ded59b5f471d97db4c4dc91918efb6204 | n2b20ded59b5f471d97db4c4dc91918efb6204 | type | n52afc3a389444a5e927b8c21689ca32cb3715 | n52afc3a389444a5e927b8c21689ca32cb3715
type | n2b20ded59b5f471d97db4c4dc91918efb6205 | n2b20ded59b5f471d97db4c4dc91918efb6205 | type | n52afc3a389444a5e927b8c21689ca32cb2726 | n52afc3a389444a5e927b8c21689ca32cb2726
type | n2b20ded59b5f471d97db4c4dc91918efb6206 | n2b20ded59b5f471d97db4c4dc91918efb6206 | type | n52afc3a389444a5e927b8c21689ca32cb3242 | n52afc3a389444a5e927b8c21689ca32cb3242
type | n2b20ded59b5f471d97db4c4dc91918efb4996 | n2b20ded59b5f471d97db4c4dc91918efb4996 | type | n52afc3a389444a5e927b8c21689ca32cb5363 | n52afc3a389444a5e927b8c21689ca32cb5363
type | n2b20ded59b5f471d97db4c4dc91918efb4997 | n2b20ded59b5f471d97db4c4dc91918efb4997 | type | n52afc3a389444a5e927b8c21689ca32cb4014 | n52afc3a389444a5e927b8c21689ca32cb4014
type | n2b20ded59b5f471d97db4c4dc91918efb1909 | n2b20ded59b5f471d97db4c4dc91918efb1909 | type | n52afc3a389444a5e927b8c21689ca32cb3064 | n52afc3a389444a5e927b8c21689ca32cb3064
type | n2b20ded59b5f471d97db4c4dc91918efb6207 | n2b20ded59b5f471d97db4c4dc91918efb6207 | type | n52afc3a389444a5e927b8c21689ca32cb3078 | n52afc3a389444a5e927b8c21689ca32cb3078
type | Thing | Thing | type | n52afc3a389444a5e927b8c21689ca32cb4297 | n52afc3a389444a5e927b8c21689ca32cb4297
type | Class | Class | type | n52afc3a389444a5e927b8c21689ca32cb5364 | n52afc3a389444a5e927b8c21689ca32cb5364
type | Equipment | Equipment | type | n52afc3a389444a5e927b8c21689ca32cb5047 | n52afc3a389444a5e927b8c21689ca32cb5047
type | HVAC_Equipment | HVAC_Equipment | type | n52afc3a389444a5e927b8c21689ca32cb5365 | n52afc3a389444a5e927b8c21689ca32cb5365
type | RVAV | RVAV | type | n52afc3a389444a5e927b8c21689ca32cb5366 | n52afc3a389444a5e927b8c21689ca32cb5366
type | Terminal_Unit | Terminal_Unit | type | n52afc3a389444a5e927b8c21689ca32cb5290 | n52afc3a389444a5e927b8c21689ca32cb5290
type | VAV | VAV | type | n52afc3a389444a5e927b8c21689ca32cb5367 | n52afc3a389444a5e927b8c21689ca32cb5367
type | Variable_Air_Volume_Box | Variable_Air_Volume_Box | type | n52afc3a389444a5e927b8c21689ca32cb5368 | n52afc3a389444a5e927b8c21689ca32cb5368
type | Variable_Air_Volume_Box_With_Reheat | Variable_Air_Volume_Box_With_Reheat | type | n52afc3a389444a5e927b8c21689ca32cb5369 | n52afc3a389444a5e927b8c21689ca32cb5369
feeds | 450_OPEN_OFFICE | 450_OPEN_OFFICE | type | n52afc3a389444a5e927b8c21689ca32cb5370 | n52afc3a389444a5e927b8c21689ca32cb5370
hasPoint | S4-12:AIR_VOLUME | S4-13:AIR_VOLUME | type | n52afc3a389444a5e927b8c21689ca32cb4241 | n52afc3a389444a5e927b8c21689ca32cb4241
hasPoint | S4-12:CLG_FLOW_MAX | S4-13:CLG_FLOW_MAX | type | n52afc3a389444a5e927b8c21689ca32cb4250 | n52afc3a389444a5e927b8c21689ca32cb4250
hasPoint | S4-12:CLG_FLOW_MIN | S4-13:CLG_FLOW_MIN | type | n52afc3a389444a5e927b8c21689ca32cb5271 | n52afc3a389444a5e927b8c21689ca32cb5271
hasPoint | S4-12:CLG_LOOPOUT | S4-13:CLG_LOOPOUT | type | n52afc3a389444a5e927b8c21689ca32cb5371 | n52afc3a389444a5e927b8c21689ca32cb5371
hasPoint | S4-12:CTL_FLOW_MAX | S4-13:CTL_FLOW_MAX | type | n52afc3a389444a5e927b8c21689ca32cb5372 | n52afc3a389444a5e927b8c21689ca32cb5372
hasPoint | S4-12:CTL_FLOW_MIN | S4-13:CTL_FLOW_MIN | type | n52afc3a389444a5e927b8c21689ca32cb5373 | n52afc3a389444a5e927b8c21689ca32cb5373
hasPoint | S4-12:CTL_STPT | S4-13:CTL_STPT | type | n52afc3a389444a5e927b8c21689ca32cb5344 | n52afc3a389444a5e927b8c21689ca32cb5344
hasPoint | S4-12:DAY_CLG_STPT | S4-13:DAY_CLG_STPT | type | n52afc3a389444a5e927b8c21689ca32cb5345 | n52afc3a389444a5e927b8c21689ca32cb5345
hasPoint | S4-12:DAY_HTG_STPT | S4-13:DAY_HTG_STPT | type | n52afc3a389444a5e927b8c21689ca32cb5374 | n52afc3a389444a5e927b8c21689ca32cb5374
hasPoint | S4-12:DAY_NGT | S4-13:DAY_NGT | type | n52afc3a389444a5e927b8c21689ca32cb5375 | n52afc3a389444a5e927b8c21689ca32cb5375
hasPoint | S4-12:DMPR_COMD | S4-13:DMPR_COMD | type | n52afc3a389444a5e927b8c21689ca32cb5376 | n52afc3a389444a5e927b8c21689ca32cb5376
hasPoint | S4-12:DMPR_POS | S4-13:DMPR_POS | type | n52afc3a389444a5e927b8c21689ca32cb5346 | n52afc3a389444a5e927b8c21689ca32cb5346
hasPoint | S4-12:HEAT_COOL | S4-13:HEAT_COOL | type | n52afc3a389444a5e927b8c21689ca32cb5377 | n52afc3a389444a5e927b8c21689ca32cb5377
hasPoint | S4-12:HTG_FLOW_MAX | S4-13:HTG_FLOW_MAX | type | n52afc3a389444a5e927b8c21689ca32cb1903 | n52afc3a389444a5e927b8c21689ca32cb1903
hasPoint | S4-12:HTG_FLOW_MIN | S4-13:HTG_FLOW_MIN | type | n52afc3a389444a5e927b8c21689ca32cb2205 | n52afc3a389444a5e927b8c21689ca32cb2205
hasPoint | S4-12:HTG_LOOPOUT | S4-13:HTG_LOOPOUT | type | n52afc3a389444a5e927b8c21689ca32cb5378 | n52afc3a389444a5e927b8c21689ca32cb5378
hasPoint | S4-12:NGT_CLG_STPT | S4-13:NGT_CLG_STPT | type | n52afc3a389444a5e927b8c21689ca32cb2337 | n52afc3a389444a5e927b8c21689ca32cb2337
hasPoint | S4-12:NGT_HTG_STPT | S4-13:NGT_HTG_STPT | type | n52afc3a389444a5e927b8c21689ca32cb1201 | n52afc3a389444a5e927b8c21689ca32cb1201
hasPoint | S4-12:SWITCH_DBAND | S4-13:SWITCH_DBAND | type | n52afc3a389444a5e927b8c21689ca32cb528 | n52afc3a389444a5e927b8c21689ca32cb528
hasPoint | S4-12:VLV_COMD | S4-13:VLV_COMD | type | n52afc3a389444a5e927b8c21689ca32cb1417 | n52afc3a389444a5e927b8c21689ca32cb1417
hasPoint | S4-12:VLV_POS | S4-13:VLV_POS | type | n52afc3a389444a5e927b8c21689ca32cb5379 | n52afc3a389444a5e927b8c21689ca32cb5379
hasTag | Box | Box | type | n52afc3a389444a5e927b8c21689ca32cb1455 | n52afc3a389444a5e927b8c21689ca32cb1455
hasTag | Equipment | Equipment | type | n52afc3a389444a5e927b8c21689ca32cb1522 | n52afc3a389444a5e927b8c21689ca32cb1522
hasTag | HVAC | HVAC | type | n52afc3a389444a5e927b8c21689ca32cb1613 | n52afc3a389444a5e927b8c21689ca32cb1613
hasTag | RVAV | RVAV | type | n52afc3a389444a5e927b8c21689ca32cb5380 | n52afc3a389444a5e927b8c21689ca32cb5380
hasTag | Reheat | Reheat | type | n52afc3a389444a5e927b8c21689ca32cb3808 | n52afc3a389444a5e927b8c21689ca32cb3808
hasTag | Terminal | Terminal | type | n52afc3a389444a5e927b8c21689ca32cb3969 | n52afc3a389444a5e927b8c21689ca32cb3969
hasTag | Unit | Unit | type | n52afc3a389444a5e927b8c21689ca32cb2993 | n52afc3a389444a5e927b8c21689ca32cb2993
hasTag | VAV | VAV | type | n52afc3a389444a5e927b8c21689ca32cb4124 | n52afc3a389444a5e927b8c21689ca32cb4124
hasTag | Variable | Variable | type | n52afc3a389444a5e927b8c21689ca32cb5349 | n52afc3a389444a5e927b8c21689ca32cb5349
hasTag | Volume | Volume | type | n52afc3a389444a5e927b8c21689ca32cb4219 | n52afc3a389444a5e927b8c21689ca32cb4219
isFedBy | AH2 | AH2 | type | Thing | Thing
isFedBy | Heat_Exchanger_System | Heat_Exchanger_System | type | Air_Temperature_Sensor | Air_Temperature_Sensor
|  |  | type | Class | Class
|  |  | type | Point | Point
|  |  | type | Sensor | Sensor
|  |  | type | Temperature_Sensor | Temperature_Sensor
|  |  | type | Zone_Air_Temperature_Sensor | Zone_Air_Temperature_Sensor
|  |  | bacnetPoint | id-7408-262-analogInput | id-7408-266-analogInput
|  |  | bacnetPoint | id-7408-31-analogInput | id-7408-34-analogInput
|  |  | hasTag | Air | Air
|  |  | hasTag | Point | Point
|  |  | hasTag | Sensor | Sensor
|  |  | hasTag | Temperature | Temperature
|  |  | hasTag | Zone | Zone
|  |  | hasUnit | http://qudt.org/vocab/unit/DEG_F | http://qudt.org/vocab/unit/DEG_F
|  |  | isPointOf | 450_OPEN_OFFICE | 450_OPEN_OFFICE
|  |  | measures | Air | Air
|  |  | measures | Temperature | Temperature
|  |  | measures | Zone_Air | Zone_Air
We can not identify these nodes, except for using node names.

## MissingOrTypoVAV
| S1-22_VAV | S1-23_VAV
type | n6dbcf46ea2bd48ff8da1523656c9f573b2557 | n6dbcf46ea2bd48ff8da1523656c9f573b2557
type | n6dbcf46ea2bd48ff8da1523656c9f573b1892 | n6dbcf46ea2bd48ff8da1523656c9f573b1892
type | n6dbcf46ea2bd48ff8da1523656c9f573b837 | n6dbcf46ea2bd48ff8da1523656c9f573b837
type | n6dbcf46ea2bd48ff8da1523656c9f573b1647 | n6dbcf46ea2bd48ff8da1523656c9f573b1647
type | n6dbcf46ea2bd48ff8da1523656c9f573b5351 | n6dbcf46ea2bd48ff8da1523656c9f573b5351
type | n6dbcf46ea2bd48ff8da1523656c9f573b954 | n6dbcf46ea2bd48ff8da1523656c9f573b954
type | n6dbcf46ea2bd48ff8da1523656c9f573b241 | n6dbcf46ea2bd48ff8da1523656c9f573b241
type | n6dbcf46ea2bd48ff8da1523656c9f573b6202 | n6dbcf46ea2bd48ff8da1523656c9f573b6202
type | n6dbcf46ea2bd48ff8da1523656c9f573b6203 | n6dbcf46ea2bd48ff8da1523656c9f573b6203
type | n6dbcf46ea2bd48ff8da1523656c9f573b6204 | n6dbcf46ea2bd48ff8da1523656c9f573b6204
type | n6dbcf46ea2bd48ff8da1523656c9f573b6205 | n6dbcf46ea2bd48ff8da1523656c9f573b6205
type | n6dbcf46ea2bd48ff8da1523656c9f573b6206 | n6dbcf46ea2bd48ff8da1523656c9f573b6206
type | n6dbcf46ea2bd48ff8da1523656c9f573b4996 | n6dbcf46ea2bd48ff8da1523656c9f573b4996
type | n6dbcf46ea2bd48ff8da1523656c9f573b4997 | n6dbcf46ea2bd48ff8da1523656c9f573b4997
type | n6dbcf46ea2bd48ff8da1523656c9f573b1909 | n6dbcf46ea2bd48ff8da1523656c9f573b1909
type | n6dbcf46ea2bd48ff8da1523656c9f573b6207 | n6dbcf46ea2bd48ff8da1523656c9f573b6207
type | Thing | Thing
type | Class | Class
type | Equipment | Equipment
type | HVAC_Equipment | HVAC_Equipment
type | RVAV | RVAV
type | Terminal_Unit | Terminal_Unit
type | VAV | VAV
type | Variable_Air_Volume_Box | Variable_Air_Volume_Box
type | Variable_Air_Volume_Box_With_Reheat | Variable_Air_Volume_Box_With_Reheat
hasPoint | S1-22:CLG_LOOPOUT | S1-23:CLG_LOOPOUT
hasPoint | S1-22:HTG_LOOPOUT | S1-23:HTG_LOOPOUT
hasTag | Box | Box
hasTag | Equipment | Equipment
hasTag | HVAC | HVAC
hasTag | RVAV | RVAV
hasTag | Reheat | Reheat
hasTag | Terminal | Terminal
hasTag | Unit | Unit
hasTag | VAV | VAV
hasTag | Variable | Variable
hasTag | Volume | Volume
isFedBy | AH2 | AH2
These VAVs don't feed any rooms.
S1-12 and S1-11 are missing. -> typo?
RM143 is missing.

## MinMax
VAV | Max_Air_Flow_Setpoint_Limit | Min_Air_Flow_Setpoint_Limit | Min>=Max
S1-01_VAV | 1200 | 840
S1-02_VAV | 772 | 220
S1-03_VAV | 220 | 700 | True
S1-04_VAV | 220 | 1088 | True
S1-05_VAV | 500 | 0
S1-06_VAV | 100 | 0
S1-07_VAV | 800 | 560
S1-08_VAV | 500 | 352
S1-09_VAV | 152 | 352 | True
S1-10_VAV | 2280 | 220
S1-13_VAV | 220 | 220 | Equal
S1-14_VAV | 1000 | 252
S1-15_VAV | 1520 | 220
S1-16_VAV | 220 | 220 | Equal
S1-17_VAV | 280 | 84
S1-18_VAV | 240 | 40
S1-19_VAV | 960 | 220
S1-20_VAV | 140 | 140 | Equal
S1-22_VAV
S1-23_VAV
S2-01_VAV | 220 | 220 | Equal
S2-02_VAV | 352 | 104
S2-03_VAV | 220 | 220 | Equal
S2-04_VAV | 200 | 60
S2-05_VAV | 776 | 220
S2-06_VAV | 2000 | 220
S2-07_VAV | 220 | 220 | Equal
S2-08_VAV | 100 | 100 | Equal
S2-09_VAV | 352 | 0
S2-10_VAV | 96 | 96 | Equal
S2-11_VAV | 1324 | 220
S2-12_VAV | 220 | 220 | Equal
S2-13_VAV | 220 | 220 | Equal
S2-14_VAV | 180 | 180 | Equal
S2-15_VAV | 576 | 220
S2-16_VAV | 1664 | 220
S2-17_VAV | 220 | 220 | Equal
S2-18_VAV | 1276 | 220
S2-19_VAV | 2200 | 220
S2-20_VAV | 400 | 220
S2-21_VAV | 900 | 220
S3-01_VAV | 1000 | 220
S3-02_VAV | 300 | 220
S3-03_VAV | 600 | 220
S3-04_VAV | 76 | 76 | Equal
S3-05_VAV | 220 | 220 | Equal
S3-06_VAV | 500 | 152
S3-07_VAV | 220 | 220 | Equal
S3-08_VAV | 220 | 152
S3-09_VAV | 220 | 220 | Equal
S3-10_VAV | 188 | 188 | Equal
S3-11_VAV | 2200 | 220
S3-12_VAV | 220 | 220 | Equal
S3-13_VAV | 500 | 0
S3-14_VAV | 352 | 0
S3-15_VAV | 220 | 220 | Equal
S3-16_VAV | 220 | 220 | Equal
S3-17_VAV | 300 | 220
S3-18_VAV | 600 | 220
S3-19_VAV | 220 | 220 | Equal
S3-20_VAV | 300 | 220
S3-21_VAV | 220 | 220 | Equal
S4-01_VAV | 100 | 100 | Equal
S4-02_VAV | 100 | 100 | Equal
S4-03_VAV | 112 | 112 | Equal
S4-04_VAV | 1000 | 112
S4-05_VAV | 1000 | 112
S4-06_VAV | 112 | 112 | Equal
S4-07_VAV | 724 | 108
S4-08_VAV | 100 | 100 | Equal
S4-09_VAV | 112 | 112 | Equal
S4-10_VAV | 100 | 0
S4-11_VAV | 112 | 112 | Equal
S4-12_VAV | 600 | 112
S4-13_VAV | 1352 | 112
S4-14_VAV | 500 | 112
S4-15_VAV | 600 | 112
S4-16_VAV | 752 | 112
S4-17_VAV | 276 | 0
S4-18_VAV | 112 | 112 | Equal
S4-19_VAV | 112 | 112 | Equal
S4-20_VAV | 112 | 112 | Equal
S4-21_VAV | 112 | 112 | Equal
S5-01_VAV | 128 | 176 | True
S5-02_VAV | 128 | 176 | True
S5-03_VAV | 220 | 212
S5-04_VAV | 156 | 212 | True
S5-05_VAV | 220 | 212
S5-06_VAV | 200 | 212 | True
S5-07_VAV | 164 | 332 | True
S5-08_VAV | 240 | 316 | True
S5-09_VAV | 228 | 212
S5-10_VAV | 1200 | 436
S5-11_VAV | 100 | 140 | True
S5-12_VAV | 220 | 528 | True
S5-13_VAV | 220 | 316 | True
S5-14_VAV | 212 | 212 | Equal
S5-15_VAV | 500 | 152
S5-16_VAV | 220 | 248 | True
S5-17_VAV | 276 | 84
S5-18_VAV | 220 | 404 | True
S5-19_VAV | 180 | 420 | True
S5-20_VAV | 204 | 212 | True
S5-21_VAV | 220 | 212
S6-01_VAV | 220 | 264 | True
S6-02_VAV | 220 | 264 | True
S6-03_VAV | 220 | 332 | True
S6-04_VAV | 52 | 124 | True
S6-05_VAV | 220 | 212
S6-06_VAV | 220 | 212
S6-07_VAV | 200 | 212 | True
S6-08_VAV | 156 | 212 | True
S6-09_VAV | 100 | 32
S6-10_VAV | 1152 | 352
S6-11_VAV | 140 | 192 | True
S6-12_VAV | 300 | 212
S6-13_VAV | 52 | 212 | True
S6-14_VAV | 500 | 152
S6-15_VAV | 120 | 332 | True
S6-16_VAV | 276 | 84
S6-17_VAV | 196 | 212 | True
S6-18_VAV | 600 | 420
S6-19_VAV | 180 | 212 | True
S6-20_VAV | 220 | 212
S7-01_VAV | 952 | 100
S7-02_VAV | 220 | 220 | Equal
S7-03_VAV | 220 | 220 | Equal
S7-04_VAV | 168 | 452 | True
S7-05_VAV | 200 | 200 | Equal
S7-06_VAV | 220 | 152
S7-07_VAV | 140 | 140 | Equal
S7-08_VAV | 188 | 188 | Equal
S7-09_VAV | 500 | 220
S7-10_VAV | 220 | 220 | Equal
S7-11_VAV | 500 | 100
S7-12_VAV | 276 | 84
S7-13_VAV | 216 | 216 | Equal
S7-14_VAV | 1500 | 220
S7-15_VAV | 180 | 180 | Equal
S7-16_VAV | 220 | 152
Min >= Max??
BACnet points are wrong?
They are "CTL_FLOW_MAX" or "CTL_FLOW_MIN".
Not cooling/heating.